TYPE UDF-50REM SMOKE VENTILATOR SPECIFICATION

I. 		PART ONE - GENERAL

1.01		SUMMARY

A.	Work included: Furnishing and installing factory fabricated smoke ventilator ( vent)

B.	Related Work: [Insert applicable specifications sections]

1.02		REFERENCES

BS EN 12101-2

Construction Product Regulation  No. 305/2011

1.03		SUBMITTALS

A.	Product Data: Provide manufacturer’s product data for all materials in this specification.

B.	Shop Drawings: Show profiles, accessories, location, and dimensions.

C.	Samples: Manufacturer to provide upon request; sized to represent material adequately.

D.	Contract Closeout: Smoke vent manufacturer shall provide the manufacturer’s Warranty prior to the contract closeout [if applicable].

1.04		PRODUCT HANDLING

A.	All materials shall be delivered in manufacturer’s original packaging.

B.	Store materials in a dry, protected, well-vented area. The contractor shall thoroughly inspect product upon receipt and report damaged material immediately to delivering carrier and note such damage on the carrier’s freight bill of lading.

C.	Remove protective wrapping immediately after installation [if applicable].

1.05		SUBSTITUTIONS

A.	Proposals for substitution products shall be accepted only from bidding contractors and not less than (10) working days before bid due date. Contractor guarantees that proposed substitution shall meet the performance and quality standards of this specification.

1.06		JOB CONDITIONS

A.	Verify that other trades with related work are complete before installing smoke vent(s).

B.	Mounting surfaces shall be straight and secure; substrates shall be of proper width.

C.	Refer to the construction documents, shop drawings, and manufacturer’s installation instructions.

D.	Coordinate installation with roof membrane and roof insulation manufacturer’s instructions before starting.

E.	Observe all appropriate OSHA safety guidelines for this work.

1.07		WARRANTY/GUARANTEE

A.	Manufacturer’s standard warranty: Materials shall be free of defects in material and workmanship for a period of five years from the date of purchase. ( electrical components 2 years) Should a part fail to function in normal use within this period, manufacturer shall furnish a new part at no charge. Special finishes, and other special equipment (if applicable) shall be warranted separately by the manufacturers of those products.

II. 		PART TWO - PRODUCTS

2.01		MANUFACTURER

A.	Bilco UK Ltd, Pavilion 7, Fornham Business Court, Hall Farm, Fornham St. Martin, 
Bury St. Edmunds, Suffolk, IP31 1SL. Tel 01284 701696, Web: www.bilcouk.co.uk

2.02		SMOKE VENT

A.	Furnish and install where indicated on plans metal smoke vent Type UDF-50REM, size width:  1500mm x length: 1620mm. Length denotes hinge sides. The smoke vent shall be double leaf and provide 1.5m² clear vent area. The smoke vent shall be pre-assembled from the manufacturer.

B. 	Performance characteristics:

1.		Covers shall be reinforced to support a minimum live load of 195 kg/m2 with a maximum deflection of 1/150th of the span.

2.		Operation of the covers shall be through a 24VDC battery backed control system that will open the   covers to the fire open position within 60 seconds and be capable of closing the covers.

3.		Operation of the covers shall not be affected by temperature.

4.		Entire vent shall be weathertight with fully welded corner joints on covers and curb.

C.	Covers: Shall be 3mm aluminium with a 100mm beaded flange with formed reinforcing members. Cover shall have a heavy extruded EPDM rubber gasket that is bonded to the cover interior to ensure a continuous seal when compressed to the top surface of the curb.

D.	Cover insulation: Shall be polyisocyanurate of 50mm thickness with a U-value of 0.47 W/m2K. Insulation shall be fully covered and protected by an aluminium liner.

E.	Curb: Shall be 305mm in height and of 3mm aluminium. The curb shall be formed with a 114mm flange with 11mm holes provided for securing to the roof deck. The curb shall be equipped with an integral metal capflashing of 2mm aluminium, fully welded at the corners, that features the Bil-Clip® flashing system, including stamped tabs, 153mm on center, to be bent inward to hold single ply roofing membrane securely in place. There shall be a fixed central drip channel through the centre section of the curb.

F.  Wind Deflectors: Shall be 4mm aluminium with 3mm EPDM gasket.

G.	Curb insulation: Shall be polyisocyanurate of 50mm thickness with a U-value of 0.47 W/m2K.

H.		Operating mechanism -  two 24VDC linear actuators per cover ( four actuators total) capable of opening the cover to the fire open position of 90 degrees.

- Hardware -

  - Heavy pintle hinges shall be provided

  - Curb mounted junction box ( 2 no.) with terminal blocks enclosed for power cable connection.

J.  Finishes: Factory finish shall be mill finish aluminium.

2.03		PERFORMANCE TO EN12101-2

Free Aerodynamic area 		1.5m²

Reliability 			RE 1000 (10,000*)

Snow Load   			SL 500

Low Ambient Temp		T (-15)

Wind Load			WL 1500

Resistance to Heat		B 300

*10,000 when used as a day to day ventilator.

III. 		PART THREE - EXECUTION

3.01		INSPECTION

A.		Verify that smoke vent installation will not disrupt other trades. Verify that the substrate is dry, clean, and free of foreign matter. Report and correct defects prior to any installation.

3.02 	INSTALLATION

A.		Submit product design drawings for review and approval to the architect or specifier before fabrication.

B.		The installer shall check as-built conditions and verify the manufacturer’s roof hatch details for accuracy to fit the application prior to fabrication. The installer shall comply with the smoke vent Manufacturer's installation instructions.

C.		The installer shall furnish mechanical fasteners consistent with the roof requirements.

25/06/13